## Alarms
id | description | siteId | deviceId | calculation | updateInterval | message | messageRtn | importanceLevel | latching | delayOn | delayOff | enabled | alarmGroupIds
g_base1_out_systemBusFault_out | IO Base 1 System Bus Fault | lazy_b | grain | ¦{register:grain:g_base1_out_systemBusFault_out}¦ | 1 | "Main IO System Bus Faulted" | "Main IO System Bus Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card01_fault_out | IO Card 1-01 Fault | lazy_b | grain | ¦{register:grain:g_base1_card01_fault_out}¦ | 1 | "Card 1-01 Faulted" | "Card 1-01 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card02_fault_out | IO Card 1-02 Fault | lazy_b | grain | ¦{register:grain:g_base1_card02_fault_out}¦ | 1 | "Card 1-02 Faulted" | "Card 1-02 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card03_fault_out | IO Card 1-03 Fault | lazy_b | grain | ¦{register:grain:g_base1_card03_fault_out}¦ | 1 | "Card 1-03 Faulted" | "Card 1-03 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card04_fault_out | IO Card 1-04 Fault | lazy_b | grain | ¦{register:grain:g_base1_card04_fault_out}¦ | 1 | "Card 1-04 Faulted" | "Card 1-04 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card05_fault_out | IO Card 1-05 Fault | lazy_b | grain | ¦{register:grain:g_base1_card05_fault_out}¦ | 1 | "Card 1-05 Faulted" | "Card 1-05 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card06_fault_out | IO Card 1-06 Fault | lazy_b | grain | ¦{register:grain:g_base1_card06_fault_out}¦ | 1 | "Card 1-06 Faulted" | "Card 1-06 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card07_fault_out | IO Card 1-07 Fault | lazy_b | grain | ¦{register:grain:g_base1_card07_fault_out}¦ | 1 | "Card 1-07 Faulted" | "Card 1-07 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card08_fault_out | IO Card 1-08 Fault | lazy_b | grain | ¦{register:grain:g_base1_card08_fault_out}¦ | 1 | "Card 1-08 Faulted" | "Card 1-08 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card09_fault_out | IO Card 1-09 Fault | lazy_b | grain | ¦{register:grain:g_base1_card09_fault_out}¦ | 1 | "Card 1-09 Faulted" | "Card 1-09 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card10_fault_out | IO Card 1-10 Fault | lazy_b | grain | ¦{register:grain:g_base1_card10_fault_out}¦ | 1 | "Card 1-10 Faulted" | "Card 1-10 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card11_fault_out | IO Card 1-11 Fault | lazy_b | grain | ¦{register:grain:g_base1_card11_fault_out}¦ | 1 | "Card 1-11 Faulted" | "Card 1-11 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card12_fault_out | IO Card 1-12 Fault | lazy_b | grain | ¦{register:grain:g_base1_card12_fault_out}¦ | 1 | "Card 1-12 Faulted" | "Card 1-12 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card13_fault_out | IO Card 1-13 Fault | lazy_b | grain | ¦{register:grain:g_base1_card13_fault_out}¦ | 1 | "Card 1-13 Faulted" | "Card 1-13 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_base1_card14_fault_out | IO Card 1-14 Fault | lazy_b | grain | ¦{register:grain:g_base1_card14_fault_out}¦ | 1 | "Card 1-14 Faulted" | "Card 1-14 Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
atGVL_dynamicAllocationFail_out | PLC Dynamic Allocation Failure | lazy_b | grain | ¦{register:grain:atGVL_dynamicAllocationFail_out}¦ | 1 | "PLC Dynamic Allocation Failure" | "PLC Dynamic Allocation Failure Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
atGVL_arrayOutOfBounds_out | PLC Array Out Of Bounds Fault | lazy_b | grain | ¦{register:grain:atGVL_arrayOutOfBounds_out}¦ | 1 | "PLC Array Out Of Bounds Fault" | "PLC Array Out Of Bounds Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_esdLoop_faults_chan_out | ESD Pushbutton Channel Fault | lazy_b | grain | ¦{register:grain:g_esdLoop_faults_chan_out}¦ | 1 | "ESD Pushbutton Channel Fault" | "ESD Pushbutton Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_esdLoop_alm_out | ESD Pushbutton | lazy_b | grain | ¦{register:grain:g_esdLoop_alm_out}¦ | 1 | "Emergency Shutdown – User Activated Pushbutton" | "ESD Pushbutton Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m05LS1_faults_chan_out | M05 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m05LS1_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 13 Limit Switch 1 Channel Fault" | "Rotary Discharge Bin 13 Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m05LS2_faults_chan_out | M05 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m05LS2_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 13 Limit Switch 2 Channel Fault" | "Rotary Discharge Bin 13 Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m06LS1_faults_chan_out | M06 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m06LS1_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 14 Limit Switch 1 Channel Fault" | "Rotary Discharge Bin 14 Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m06LS2_faults_chan_out | M06 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m06LS2_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 14 Limit Switch 2 Channel Fault" | "Rotary Discharge Bin 14 Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m07LS1_faults_chan_out | M07 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m07LS1_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 15 Limit Switch 1 Channel Fault" | "Rotary Discharge Bin 15 Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m07LS2_faults_chan_out | M07 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m07LS2_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 15 Limit Switch 2 Channel Fault" | "Rotary Discharge Bin 15 Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m08LS1_faults_chan_out | M08 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m08LS1_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 16 Limit Switch 1 Channel Fault" | "Rotary Discharge Bin 16 Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m08LS2_faults_chan_out | M08 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m08LS2_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 16 Limit Switch 2 Channel Fault" | "Rotary Discharge Bin 16 Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m09LS1_faults_chan_out | M09 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m09LS1_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 17 Limit Switch 1 Channel Fault" | "Rotary Discharge Bin 17 Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m09LS2_faults_chan_out | M09 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m09LS2_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 17 Limit Switch 2 Channel Fault" | "Rotary Discharge Bin 17 Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m10LS1_faults_chan_out | M10 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m10LS1_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 18 Limit Switch 1 Channel Fault" | "Rotary Discharge Bin 18 Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m10LS2_faults_chan_out | M10 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m10LS2_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 18 Limit Switch 2 Channel Fault" | "Rotary Discharge Bin 18 Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m11LS1_faults_chan_out | M11 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m11LS1_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 19 Limit Switch 1 Channel Fault" | "Rotary Discharge Bin 19 Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m11LS2_faults_chan_out | M11 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m11LS2_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 19 Limit Switch 2 Channel Fault" | "Rotary Discharge Bin 19 Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m12LS1_faults_chan_out | M12 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m12LS1_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 20 Limit Switch 1 Channel Fault" | "Rotary Discharge Bin 20 Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m12LS2_faults_chan_out | M12 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m12LS2_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 20 Limit Switch 2 Channel Fault" | "Rotary Discharge Bin 20 Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_01LS1_faults_chan_out | M32-01 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m32_01LS1_faults_chan_out}¦ | 1 | "3 Way Valve Limit Switch 1 Channel Fault" | "3 Way Valve Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_01LS2_faults_chan_out | M32-01 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m32_01LS2_faults_chan_out}¦ | 1 | "3 Way Valve Limit Switch 2 Channel Fault" | "3 Way Valve Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_02LS1_faults_chan_out | M32-02 Limit Switch 1 Channel Fault | lazy_b | grain | ¦{register:grain:g_m32_02LS1_faults_chan_out}¦ | 1 | "3 Way Valve Limit Switch 1 Channel Fault" | "3 Way Valve Limit Switch 1 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_02LS2_faults_chan_out | M32-02 Limit Switch 2 Channel Fault | lazy_b | grain | ¦{register:grain:g_m32_02LS2_faults_chan_out}¦ | 1 | "3 Way Valve Limit Switch 2 Channel Fault" | "3 Way Valve Limit Switch 2 Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m51BinSns_faults_chan_out | M51 Bin Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m51BinSns_faults_chan_out}¦ | 1 | "Bin Fan 13 Sensor Channel Fault" | "Bin Fan 13 Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m52BinSns_faults_chan_out | M52 Bin Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m52BinSns_faults_chan_out}¦ | 1 | "Bin Fan 14 Sensor Channel Fault" | "Bin Fan 14 Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m53BinSns_faults_chan_out | M53 Bin Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m53BinSns_faults_chan_out}¦ | 1 | "Bin Fan 15 Sensor Channel Fault" | "Bin Fan 15 Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m54BinSns_faults_chan_out | M54 Bin Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m54BinSns_faults_chan_out}¦ | 1 | "Bin Fan 16 Sensor Channel Fault" | "Bin Fan 16 Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m55BinSns_faults_chan_out | M55 Bin Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m55BinSns_faults_chan_out}¦ | 1 | "Bin Fan 17 Sensor Channel Fault" | "Bin Fan 17 Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m56BinSns_faults_chan_out | M56 Bin Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m56BinSns_faults_chan_out}¦ | 1 | "Bin Fan 18 Sensor Channel Fault" | "Bin Fan 18 Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m57BinSns_faults_chan_out | M57 Bin Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m57BinSns_faults_chan_out}¦ | 1 | "Bin Fan 19 Sensor Channel Fault" | "Bin Fan 19 Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m58BinSns_faults_chan_out | M58 Bin Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m58BinSns_faults_chan_out}¦ | 1 | "Bin Fan 20 Sensor Channel Fault" | "Bin Fan 20 Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m31LSHH_faults_chan_out | M31 High-High Level Switch Channel Fault | lazy_b | grain | ¦{register:grain:g_m31LSHH_faults_chan_out}¦ | 1 | "Reclaim Grain Pump High-High Level Switch Channel Fault" | "Reclaim Grain Pump High-High Level Switch Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m31LSHH_alm_out | M31 High-High Level Alarm | lazy_b | grain | ¦{register:grain:g_m31LSHH_alm_out}¦ | 1 | "Reclaim Grain Pump High-High Level Alarm" | "Reclaim Grain Pump High-High Level Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_pbRecSrt_faults_chan_out | Receiving Start Pushbutton Channel Fault | lazy_b | grain | ¦{register:grain:g_pbRecSrt_faults_chan_out}¦ | 1 | "Receiving Start Pushbutton Channel Fault" | "Receiving Start Pushbutton Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_pbRecStp_faults_chan_out | Receiving Stop Pushbutton Channel Fault | lazy_b | grain | ¦{register:grain:g_pbRecStp_faults_chan_out}¦ | 1 | "Receiving Stop Pushbutton Channel Fault" | "Receiving Stop Pushbutton Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_pbRecRpdStp_faults_chan_out | Receiving Rapid Stop Pushbutton Channel Fault | lazy_b | grain | ¦{register:grain:g_pbRecRpdStp_faults_chan_out}¦ | 1 | "Receiving Rapid Stop Pushbutton Channel Fault" | "Receiving Rapid Stop Pushbutton Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_pbRclRpdStp_faults_chan_out | Reclaim Rapid Stop Pushbutton Channel Fault | lazy_b | grain | ¦{register:grain:g_pbRclRpdStp_faults_chan_out}¦ | 1 | "Reclaim Rapid Stop Pushbutton Channel Fault" | "Reclaim Rapid Stop Pushbutton Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_pbLdRpdStp_faults_chan_out | Loadout Rapid Stop Pushbutton Channel Fault | lazy_b | grain | ¦{register:grain:g_pbLdRpdStp_faults_chan_out}¦ | 1 | "Loadout Rapid Stop Pushbutton Channel Fault" | "Loadout Rapid Stop Pushbutton Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m01Ovld_faults_chan_out | M01 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m01Ovld_faults_chan_out}¦ | 1 | "Truck Drag Overload Channel Fault" | "Truck Drag Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m01Ovld_alm_out | M01 Overload Trip | lazy_b | grain | ¦{register:grain:g_m01Ovld_alm_out}¦ | 1 | "Truck Drag Overload Trip" | "Truck Drag Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m02Ovld_faults_chan_out | M02 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m02Ovld_faults_chan_out}¦ | 1 | "Receiving Drag Overload Channel Fault" | "Receiving Drag Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m02Ovld_alm_out | M02 Overload Trip | lazy_b | grain | ¦{register:grain:g_m02Ovld_alm_out}¦ | 1 | "Receiving Drag Overload Trip" | "Receiving Drag Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m03Ovld_faults_chan_out | M03 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m03Ovld_faults_chan_out}¦ | 1 | "Receiving Grain Pump Overload Channel Fault" | "Receiving Grain Pump Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m03Ovld_alm_out | M03 Overload Trip | lazy_b | grain | ¦{register:grain:g_m03Ovld_alm_out}¦ | 1 | "Receiving Grain Pump Overload Trip" | "Receiving Grain Pump Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m04_01Ovld_faults_chan_out | M04-01 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m04_01Ovld_faults_chan_out}¦ | 1 | "Distribution Loop (Motor 1) Overload Channel Fault" | "Distribution Loop (Motor 1) Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m04_01Ovld_alm_out | M04-01 Overload Trip | lazy_b | grain | ¦{register:grain:g_m04_01Ovld_alm_out}¦ | 1 | "Distribution Loop (Motor 1) Overload Trip" | "Distribution Loop (Motor 1) Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m04_02Ovld_faults_chan_out | M04-02 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m04_02Ovld_faults_chan_out}¦ | 1 | "Distribution Loop (Motor 2) Overload Channel Fault" | "Distribution Loop (Motor 2) Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m04_02Ovld_alm_out | M04-02 Overload Trip | lazy_b | grain | ¦{register:grain:g_m04_02Ovld_alm_out}¦ | 1 | "Distribution Loop (Motor 2) Overload Trip" | "Distribution Loop (Motor 2) Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m05Ovld_faults_chan_out | M05 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m05Ovld_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 13 Overload Channel Fault" | "Rotary Discharge Bin 13 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m05Ovld_alm_out | M05 Overload Trip | lazy_b | grain | ¦{register:grain:g_m05Ovld_alm_out}¦ | 1 | "Rotary Discharge Bin 13 Overload Trip" | "Rotary Discharge Bin 13 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m06Ovld_faults_chan_out | M06 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m06Ovld_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 14 Overload Channel Fault" | "Rotary Discharge Bin 14 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m06Ovld_alm_out | M06 Overload Trip | lazy_b | grain | ¦{register:grain:g_m06Ovld_alm_out}¦ | 1 | "Rotary Discharge Bin 14 Overload Trip" | "Rotary Discharge Bin 14 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m07Ovld_faults_chan_out | M07 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m07Ovld_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 15 Overload Channel Fault" | "Rotary Discharge Bin 15 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m07Ovld_alm_out | M07 Overload Trip | lazy_b | grain | ¦{register:grain:g_m07Ovld_alm_out}¦ | 1 | "Rotary Discharge Bin 15 Overload Trip" | "Rotary Discharge Bin 15 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m08Ovld_faults_chan_out | M08 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m08Ovld_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 16 Overload Channel Fault" | "Rotary Discharge Bin 16 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m08Ovld_alm_out | M08 Overload Trip | lazy_b | grain | ¦{register:grain:g_m08Ovld_alm_out}¦ | 1 | "Rotary Discharge Bin 16 Overload Trip" | "Rotary Discharge Bin 16 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m09Ovld_faults_chan_out | M09 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m09Ovld_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 17 Overload Channel Fault" | "Rotary Discharge Bin 17 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m09Ovld_alm_out | M09 Overload Trip | lazy_b | grain | ¦{register:grain:g_m09Ovld_alm_out}¦ | 1 | "Rotary Discharge Bin 17 Overload Trip" | "Rotary Discharge Bin 17 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m10Ovld_faults_chan_out | M10 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m10Ovld_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 18 Overload Channel Fault" | "Rotary Discharge Bin 18 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m10Ovld_alm_out | M10 Overload Trip | lazy_b | grain | ¦{register:grain:g_m10Ovld_alm_out}¦ | 1 | "Rotary Discharge Bin 18 Overload Trip" | "Rotary Discharge Bin 18 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m11Ovld_faults_chan_out | M11 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m11Ovld_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 19 Overload Channel Fault" | "Rotary Discharge Bin 19 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m11Ovld_alm_out | M11 Overload Trip | lazy_b | grain | ¦{register:grain:g_m11Ovld_alm_out}¦ | 1 | "Rotary Discharge Bin 19 Overload Trip" | "Rotary Discharge Bin 19 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m12Ovld_faults_chan_out | M12 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m12Ovld_faults_chan_out}¦ | 1 | "Rotary Discharge Bin 20 Overload Channel Fault" | "Rotary Discharge Bin 20 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m12Ovld_alm_out | M12 Overload Trip | lazy_b | grain | ¦{register:grain:g_m12Ovld_alm_out}¦ | 1 | "Rotary Discharge Bin 20 Overload Trip" | "Rotary Discharge Bin 20 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m21Ovld_faults_chan_out | M21 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m21Ovld_faults_chan_out}¦ | 1 | "Reclaim Auger Bin 13 Overload Channel Fault" | "Reclaim Auger Bin 13 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m21Ovld_alm_out | M21 Overload Trip | lazy_b | grain | ¦{register:grain:g_m21Ovld_alm_out}¦ | 1 | "Reclaim Auger Bin 13 Overload Trip" | "Reclaim Auger Bin 13 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m22Ovld_faults_chan_out | M22 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m22Ovld_faults_chan_out}¦ | 1 | "Reclaim Auger Bin 14 Overload Channel Fault" | "Reclaim Auger Bin 14 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m22Ovld_alm_out | M22 Overload Trip | lazy_b | grain | ¦{register:grain:g_m22Ovld_alm_out}¦ | 1 | "Reclaim Auger Bin 14 Overload Trip" | "Reclaim Auger Bin 14 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m23Ovld_faults_chan_out | M23 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m23Ovld_faults_chan_out}¦ | 1 | "Reclaim Auger Bin 15 Overload Channel Fault" | "Reclaim Auger Bin 15 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m23Ovld_alm_out | M23 Overload Trip | lazy_b | grain | ¦{register:grain:g_m23Ovld_alm_out}¦ | 1 | "Reclaim Auger Bin 15 Overload Trip" | "Reclaim Auger Bin 15 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m24Ovld_faults_chan_out | M24 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m24Ovld_faults_chan_out}¦ | 1 | "Reclaim Auger Bin 16 Overload Channel Fault" | "Reclaim Auger Bin 16 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m24Ovld_alm_out | M24 Overload Trip | lazy_b | grain | ¦{register:grain:g_m24Ovld_alm_out}¦ | 1 | "Reclaim Auger Bin 16 Overload Trip" | "Reclaim Auger Bin 16 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m25Ovld_faults_chan_out | M25 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m25Ovld_faults_chan_out}¦ | 1 | "Reclaim Auger Bin 17 Overload Channel Fault" | "Reclaim Auger Bin 17 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m25Ovld_alm_out | M25 Overload Trip | lazy_b | grain | ¦{register:grain:g_m25Ovld_alm_out}¦ | 1 | "Reclaim Auger Bin 17 Overload Trip" | "Reclaim Auger Bin 17 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m26Ovld_faults_chan_out | M26 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m26Ovld_faults_chan_out}¦ | 1 | "Reclaim Auger Bin 18 Overload Channel Fault" | "Reclaim Auger Bin 18 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m26Ovld_alm_out | M26 Overload Trip | lazy_b | grain | ¦{register:grain:g_m26Ovld_alm_out}¦ | 1 | "Reclaim Auger Bin 18 Overload Trip" | "Reclaim Auger Bin 18 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m27Ovld_faults_chan_out | M27 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m27Ovld_faults_chan_out}¦ | 1 | "Reclaim Auger Bin 19 Overload Channel Fault" | "Reclaim Auger Bin 19 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m27Ovld_alm_out | M27 Overload Trip | lazy_b | grain | ¦{register:grain:g_m27Ovld_alm_out}¦ | 1 | "Reclaim Auger Bin 19 Overload Trip" | "Reclaim Auger Bin 19 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m28Ovld_faults_chan_out | M28 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m28Ovld_faults_chan_out}¦ | 1 | "Reclaim Auger Bin 20 Overload Channel Fault" | "Reclaim Auger Bin 20 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m28Ovld_alm_out | M28 Overload Trip | lazy_b | grain | ¦{register:grain:g_m28Ovld_alm_out}¦ | 1 | "Reclaim Auger Bin 20 Overload Trip" | "Reclaim Auger Bin 20 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m29Ovld_faults_chan_out | M29 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m29Ovld_faults_chan_out}¦ | 1 | "Reclaim Drag North Overload Channel Fault" | "Reclaim Drag North Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m29Ovld_alm_out | M29 Overload Trip | lazy_b | grain | ¦{register:grain:g_m29Ovld_alm_out}¦ | 1 | "Reclaim Drag North Overload Trip" | "Reclaim Drag North Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m30Ovld_faults_chan_out | M30 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m30Ovld_faults_chan_out}¦ | 1 | "Reclaim Drag South Overload Channel Fault" | "Reclaim Drag South Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m30Ovld_alm_out | M30 Overload Trip | lazy_b | grain | ¦{register:grain:g_m30Ovld_alm_out}¦ | 1 | "Reclaim Drag South Overload Trip" | "Reclaim Drag South Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m31Ovld_faults_chan_out | M31 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m31Ovld_faults_chan_out}¦ | 1 | "Reclaim Grain Pump Overload Channel Fault" | "Reclaim Grain Pump Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m31Ovld_alm_out | M31 Overload Trip | lazy_b | grain | ¦{register:grain:g_m31Ovld_alm_out}¦ | 1 | "Reclaim Grain Pump Overload Trip" | "Reclaim Grain Pump Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_01Ovld_faults_chan_out | M32-01 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m32_01Ovld_faults_chan_out}¦ | 1 | "3 Way Valve Overload Channel Fault" | "3 Way Valve Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_01Ovld_alm_out | M32-01 Overload Trip | lazy_b | grain | ¦{register:grain:g_m32_01Ovld_alm_out}¦ | 1 | "3 Way Valve Overload Trip" | "3 Way Valve Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_02Ovld_faults_chan_out | M32-02 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m32_02Ovld_faults_chan_out}¦ | 1 | "3 Way Valve Overload Channel Fault" | "3 Way Valve Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_02Ovld_alm_out | M32-02 Overload Trip | lazy_b | grain | ¦{register:grain:g_m32_02Ovld_alm_out}¦ | 1 | "3 Way Valve Overload Trip" | "3 Way Valve Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m41Ovld_faults_chan_out | M41 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m41Ovld_faults_chan_out}¦ | 1 | "Loadout Gate Overload Channel Fault" | "Loadout Gate Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m41Ovld_alm_out | M41 Overload Trip | lazy_b | grain | ¦{register:grain:g_m41Ovld_alm_out}¦ | 1 | "Loadout Gate Overload Trip" | "Loadout Gate Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m51Ovld_faults_chan_out | M51 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m51Ovld_faults_chan_out}¦ | 1 | "Bin Fan 13 Overload Channel Fault" | "Bin Fan 13 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m51Ovld_alm_out | M51 Overload Trip | lazy_b | grain | ¦{register:grain:g_m51Ovld_alm_out}¦ | 1 | "Bin Fan 13 Overload Trip" | "Bin Fan 13 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m52Ovld_faults_chan_out | M52 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m52Ovld_faults_chan_out}¦ | 1 | "Bin Fan 14 Overload Channel Fault" | "Bin Fan 14 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m52Ovld_alm_out | M52 Overload Trip | lazy_b | grain | ¦{register:grain:g_m52Ovld_alm_out}¦ | 1 | "Bin Fan 14 Overload Trip" | "Bin Fan 14 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m53Ovld_faults_chan_out | M53 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m53Ovld_faults_chan_out}¦ | 1 | "Bin Fan 15 Overload Channel Fault" | "Bin Fan 15 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m53Ovld_alm_out | M53 Overload Trip | lazy_b | grain | ¦{register:grain:g_m53Ovld_alm_out}¦ | 1 | "Bin Fan 15 Overload Trip" | "Bin Fan 15 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m54Ovld_faults_chan_out | M54 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m54Ovld_faults_chan_out}¦ | 1 | "Bin Fan 16 Overload Channel Fault" | "Bin Fan 16 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m54Ovld_alm_out | M54 Overload Trip | lazy_b | grain | ¦{register:grain:g_m54Ovld_alm_out}¦ | 1 | "Bin Fan 16 Overload Trip" | "Bin Fan 16 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m55Ovld_faults_chan_out | M55 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m55Ovld_faults_chan_out}¦ | 1 | "Bin Fan 17 Overload Channel Fault" | "Bin Fan 17 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m55Ovld_alm_out | M55 Overload Trip | lazy_b | grain | ¦{register:grain:g_m55Ovld_alm_out}¦ | 1 | "Bin Fan 17 Overload Trip" | "Bin Fan 17 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m56Ovld_faults_chan_out | M56 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m56Ovld_faults_chan_out}¦ | 1 | "Bin Fan 18 Overload Channel Fault" | "Bin Fan 18 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m56Ovld_alm_out | M56 Overload Trip | lazy_b | grain | ¦{register:grain:g_m56Ovld_alm_out}¦ | 1 | "Bin Fan 18 Overload Trip" | "Bin Fan 18 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m57Ovld_faults_chan_out | M57 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m57Ovld_faults_chan_out}¦ | 1 | "Bin Fan 19 Overload Channel Fault" | "Bin Fan 19 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m57Ovld_alm_out | M57 Overload Trip | lazy_b | grain | ¦{register:grain:g_m57Ovld_alm_out}¦ | 1 | "Bin Fan 19 Overload Trip" | "Bin Fan 19 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m58Ovld_faults_chan_out | M58 Overload Channel Fault | lazy_b | grain | ¦{register:grain:g_m58Ovld_faults_chan_out}¦ | 1 | "Bin Fan 20 Overload Channel Fault" | "Bin Fan 20 Overload Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m58Ovld_alm_out | M58 Overload Trip | lazy_b | grain | ¦{register:grain:g_m58Ovld_alm_out}¦ | 1 | "Bin Fan 20 Overload Trip" | "Bin Fan 20 Overload Reset" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m02RunCmd_fault_out | M02 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m02RunCmd_fault_out}¦ | 1 | "Receiving Drag Run Command Fault" | "Receiving Drag Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m05CloseCmd_fault_out | M05 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m05CloseCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 13 Close Command Fault" | "Rotary Discharge Bin 13 Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m05OpenCmd_fault_out | M05 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m05OpenCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 13 Open Command Fault" | "Rotary Discharge Bin 13 Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m06CloseCmd_fault_out | M06 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m06CloseCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 14 Close Command Fault" | "Rotary Discharge Bin 14 Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m06OpenCmd_fault_out | M06 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m06OpenCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 14 Open Command Fault" | "Rotary Discharge Bin 14 Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m07CloseCmd_fault_out | M07 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m07CloseCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 15 Close Command Fault" | "Rotary Discharge Bin 15 Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m07OpenCmd_fault_out | M07 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m07OpenCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 15 Open Command Fault" | "Rotary Discharge Bin 15 Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m08CloseCmd_fault_out | M08 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m08CloseCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 16 Close Command Fault" | "Rotary Discharge Bin 16 Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m08OpenCmd_fault_out | M08 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m08OpenCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 16 Open Command Fault" | "Rotary Discharge Bin 16 Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m09CloseCmd_fault_out | M09 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m09CloseCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 17 Close Command Fault" | "Rotary Discharge Bin 17 Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m09OpenCmd_fault_out | M09 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m09OpenCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 17 Open Command Fault" | "Rotary Discharge Bin 17 Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m10CloseCmd_fault_out | M10 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m10CloseCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 18 Close Command Fault" | "Rotary Discharge Bin 18 Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m10OpenCmd_fault_out | M10 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m10OpenCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 18 Open Command Fault" | "Rotary Discharge Bin 18 Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m11CloseCmd_fault_out | M11 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m11CloseCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 19 Close Command Fault" | "Rotary Discharge Bin 19 Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m11OpenCmd_fault_out | M11 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m11OpenCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 19 Open Command Fault" | "Rotary Discharge Bin 19 Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m12CloseCmd_fault_out | M12 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m12CloseCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 20 Close Command Fault" | "Rotary Discharge Bin 20 Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m12OpenCmd_fault_out | M12 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m12OpenCmd_fault_out}¦ | 1 | "Rotary Discharge Bin 20 Open Command Fault" | "Rotary Discharge Bin 20 Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m21RunCmd_fault_out | M21 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m21RunCmd_fault_out}¦ | 1 | "Reclaim Auger Bin 13 Run Command Fault" | "Reclaim Auger Bin 13 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m22RunCmd_fault_out | M22 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m22RunCmd_fault_out}¦ | 1 | "Reclaim Auger Bin 14 Run Command Fault" | "Reclaim Auger Bin 14 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m23RunCmd_fault_out | M23 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m23RunCmd_fault_out}¦ | 1 | "Reclaim Auger Bin 15 Run Command Fault" | "Reclaim Auger Bin 15 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m24RunCmd_fault_out | M24 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m24RunCmd_fault_out}¦ | 1 | "Reclaim Auger Bin 16 Run Command Fault" | "Reclaim Auger Bin 16 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m25RunCmd_fault_out | M25 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m25RunCmd_fault_out}¦ | 1 | "Reclaim Auger Bin 17 Run Command Fault" | "Reclaim Auger Bin 17 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m26RunCmd_fault_out | M26 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m26RunCmd_fault_out}¦ | 1 | "Reclaim Auger Bin 18 Run Command Fault" | "Reclaim Auger Bin 18 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m27RunCmd_fault_out | M27 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m27RunCmd_fault_out}¦ | 1 | "Reclaim Auger Bin 19 Run Command Fault" | "Reclaim Auger Bin 19 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m28RunCmd_fault_out | M28 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m28RunCmd_fault_out}¦ | 1 | "Reclaim Auger Bin 20 Run Command Fault" | "Reclaim Auger Bin 20 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m29RunCmd_fault_out | M29 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m29RunCmd_fault_out}¦ | 1 | "Reclaim Drag North Run Command Fault" | "Reclaim Drag North Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m30RunCmd_fault_out | M30 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m30RunCmd_fault_out}¦ | 1 | "Reclaim Drag South Run Command Fault" | "Reclaim Drag South Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_01CloseCmd_fault_out | M32-01 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m32_01CloseCmd_fault_out}¦ | 1 | "3 Way Valve Close Command Fault" | "3 Way Valve Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_01OpenCmd_fault_out | M32-01 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m32_01OpenCmd_fault_out}¦ | 1 | "3 Way Valve Open Command Fault" | "3 Way Valve Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_02CloseCmd_fault_out | M32-02 Close Command Fault | lazy_b | grain | ¦{register:grain:g_m32_02CloseCmd_fault_out}¦ | 1 | "3 Way Valve Close Command Fault" | "3 Way Valve Close Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m32_02OpenCmd_fault_out | M32-02 Open Command Fault | lazy_b | grain | ¦{register:grain:g_m32_02OpenCmd_fault_out}¦ | 1 | "3 Way Valve Open Command Fault" | "3 Way Valve Open Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m51RunCmd_fault_out | M51 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m51RunCmd_fault_out}¦ | 1 | "Bin Fan 13 Run Command Fault" | "Bin Fan 13 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m52RunCmd_fault_out | M52 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m52RunCmd_fault_out}¦ | 1 | "Bin Fan 14 Run Command Fault" | "Bin Fan 14 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m53RunCmd_fault_out | M53 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m53RunCmd_fault_out}¦ | 1 | "Bin Fan 15 Run Command Fault" | "Bin Fan 15 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m54RunCmd_fault_out | M54 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m54RunCmd_fault_out}¦ | 1 | "Bin Fan 16 Run Command Fault" | "Bin Fan 16 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m55RunCmd_fault_out | M55 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m55RunCmd_fault_out}¦ | 1 | "Bin Fan 17 Run Command Fault" | "Bin Fan 17 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m56RunCmd_fault_out | M56 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m56RunCmd_fault_out}¦ | 1 | "Bin Fan 18 Run Command Fault" | "Bin Fan 18 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m57RunCmd_fault_out | M57 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m57RunCmd_fault_out}¦ | 1 | "Bin Fan 19 Run Command Fault" | "Bin Fan 19 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m58RunCmd_fault_out | M58 Run Command Fault | lazy_b | grain | ¦{register:grain:g_m58RunCmd_fault_out}¦ | 1 | "Bin Fan 20 Run Command Fault" | "Bin Fan 20 Run Command Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_recRdyLite_fault_out | Receiving Ready Light Output Fault | lazy_b | grain | ¦{register:grain:g_recRdyLite_fault_out}¦ | 1 | "Receiving Ready Light Output Fault" | "Receiving Ready Light Output Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_recFltLite_fault_out | Receiving Fault Light Output Fault | lazy_b | grain | ¦{register:grain:g_recFltLite_fault_out}¦ | 1 | "Receiving Fault Light Output Fault" | "Receiving Fault Light Output Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin13Lvl_faults_over_out | Bin 13 Level Sensor Overrange Fault | lazy_b | grain | ¦{register:grain:g_bin13Lvl_faults_over_out}¦ | 1 | "Bin 13 Level Sensor Overrange Fault, reading " + Math.round(¦{register:grain:g_bin13Lvl_out_eu}¦) + "%" | "Bin 13 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin13Lvl_faults_under_out | Bin 13 Level Sensor Underrange Fault | lazy_b | grain | ¦{register:grain:g_bin13Lvl_faults_under_out}¦ | 1 | "Bin 13 Level Sensor Underrange Fault, reading " + Math.round(¦{register:grain:g_bin13Lvl_out_eu}¦) + "%" | "Bin 13 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin13Lvl_faults_chan_out | Bin 13 Level Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_bin13Lvl_faults_chan_out}¦ | 1 | "Bin 13 Level Sensor Channel Fault" | "Bin 13 Level Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin13Lvl_limits_hihi_alm_out | Bin 13 Level High-High Alarm | lazy_b | grain | ¦{register:grain:g_bin13Lvl_limits_hihi_alm_out}¦ | 1 | "Bin 13 Level High-High Alarm, at " + Math.round(¦{register:grain:g_bin13Lvl_out_eu}¦) + "%" | "Bin 13 Level High-High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin13Lvl_limits_hi_alm_out | Bin 13 Level High Alarm | lazy_b | grain | ¦{register:grain:g_bin13Lvl_limits_hi_alm_out}¦ | 1 | "Bin 13 Level High Alarm, at " + Math.round(¦{register:grain:g_bin13Lvl_out_eu}¦) + "%" | "Bin 13 Level High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin13Lvl_limits_lo_alm_out | Bin 13 Level Low Alarm | lazy_b | grain | ¦{register:grain:g_bin13Lvl_limits_lo_alm_out}¦ | 1 | "Bin 13 Level Low Alarm, at " + Math.round(¦{register:grain:g_bin13Lvl_out_eu}¦) + "%" | "Bin 13 Level Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin13Lvl_limits_lolo_alm_out | Bin 13 Level Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_bin13Lvl_limits_lolo_alm_out}¦ | 1 | "Bin 13 Level Low-Low Alarm, at " + Math.round(¦{register:grain:g_bin13Lvl_out_eu}¦) + "%" | "Bin 13 Level Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin14Lvl_faults_over_out | Bin 14 Level Sensor Overrange Fault | lazy_b | grain | ¦{register:grain:g_bin14Lvl_faults_over_out}¦ | 1 | "Bin 14 Level Sensor Overrange Fault, reading " + Math.round(¦{register:grain:g_bin14Lvl_out_eu}¦) + "%" | "Bin 14 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin14Lvl_faults_under_out | Bin 14 Level Sensor Underrange Fault | lazy_b | grain | ¦{register:grain:g_bin14Lvl_faults_under_out}¦ | 1 | "Bin 14 Level Sensor Underrange Fault, reading " + Math.round(¦{register:grain:g_bin14Lvl_out_eu}¦) + "%" | "Bin 14 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin14Lvl_faults_chan_out | Bin 14 Level Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_bin14Lvl_faults_chan_out}¦ | 1 | "Bin 14 Level Sensor Channel Fault" | "Bin 14 Level Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin14Lvl_limits_hihi_alm_out | Bin 14 Level High-High Alarm | lazy_b | grain | ¦{register:grain:g_bin14Lvl_limits_hihi_alm_out}¦ | 1 | "Bin 14 Level High-High Alarm, at " + Math.round(¦{register:grain:g_bin14Lvl_out_eu}¦) + "%" | "Bin 14 Level High-High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin14Lvl_limits_hi_alm_out | Bin 14 Level High Alarm | lazy_b | grain | ¦{register:grain:g_bin14Lvl_limits_hi_alm_out}¦ | 1 | "Bin 14 Level High Alarm, at " + Math.round(¦{register:grain:g_bin14Lvl_out_eu}¦) + "%" | "Bin 14 Level High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin14Lvl_limits_lo_alm_out | Bin 14 Level Low Alarm | lazy_b | grain | ¦{register:grain:g_bin14Lvl_limits_lo_alm_out}¦ | 1 | "Bin 14 Level Low Alarm, at " + Math.round(¦{register:grain:g_bin14Lvl_out_eu}¦) + "%" | "Bin 14 Level Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin14Lvl_limits_lolo_alm_out | Bin 14 Level Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_bin14Lvl_limits_lolo_alm_out}¦ | 1 | "Bin 14 Level Low-Low Alarm, at " + Math.round(¦{register:grain:g_bin14Lvl_out_eu}¦) + "%" | "Bin 14 Level Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin15Lvl_faults_over_out | Bin 15 Level Sensor Overrange Fault | lazy_b | grain | ¦{register:grain:g_bin15Lvl_faults_over_out}¦ | 1 | "Bin 15 Level Sensor Overrange Fault, reading " + Math.round(¦{register:grain:g_bin15Lvl_out_eu}¦) + "%" | "Bin 15 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin15Lvl_faults_under_out | Bin 15 Level Sensor Underrange Fault | lazy_b | grain | ¦{register:grain:g_bin15Lvl_faults_under_out}¦ | 1 | "Bin 15 Level Sensor Underrange Fault, reading " + Math.round(¦{register:grain:g_bin15Lvl_out_eu}¦) + "%" | "Bin 15 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin15Lvl_faults_chan_out | Bin 15 Level Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_bin15Lvl_faults_chan_out}¦ | 1 | "Bin 15 Level Sensor Channel Fault" | "Bin 15 Level Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin15Lvl_limits_hihi_alm_out | Bin 15 Level High-High Alarm | lazy_b | grain | ¦{register:grain:g_bin15Lvl_limits_hihi_alm_out}¦ | 1 | "Bin 15 Level High-High Alarm, at " + Math.round(¦{register:grain:g_bin15Lvl_out_eu}¦) + "%" | "Bin 15 Level High-High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin15Lvl_limits_hi_alm_out | Bin 15 Level High Alarm | lazy_b | grain | ¦{register:grain:g_bin15Lvl_limits_hi_alm_out}¦ | 1 | "Bin 15 Level High Alarm, at " + Math.round(¦{register:grain:g_bin15Lvl_out_eu}¦) + "%" | "Bin 15 Level High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin15Lvl_limits_lo_alm_out | Bin 15 Level Low Alarm | lazy_b | grain | ¦{register:grain:g_bin15Lvl_limits_lo_alm_out}¦ | 1 | "Bin 15 Level Low Alarm, at " + Math.round(¦{register:grain:g_bin15Lvl_out_eu}¦) + "%" | "Bin 15 Level Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin15Lvl_limits_lolo_alm_out | Bin 15 Level Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_bin15Lvl_limits_lolo_alm_out}¦ | 1 | "Bin 15 Level Low-Low Alarm, at " + Math.round(¦{register:grain:g_bin15Lvl_out_eu}¦) + "%" | "Bin 15 Level Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin16Lvl_faults_over_out | Bin 16 Level Sensor Overrange Fault | lazy_b | grain | ¦{register:grain:g_bin16Lvl_faults_over_out}¦ | 1 | "Bin 16 Level Sensor Overrange Fault, reading " + Math.round(¦{register:grain:g_bin16Lvl_out_eu}¦) + "%" | "Bin 16 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin16Lvl_faults_under_out | Bin 16 Level Sensor Underrange Fault | lazy_b | grain | ¦{register:grain:g_bin16Lvl_faults_under_out}¦ | 1 | "Bin 16 Level Sensor Underrange Fault, reading " + Math.round(¦{register:grain:g_bin16Lvl_out_eu}¦) + "%" | "Bin 16 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin16Lvl_faults_chan_out | Bin 16 Level Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_bin16Lvl_faults_chan_out}¦ | 1 | "Bin 16 Level Sensor Channel Fault" | "Bin 16 Level Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin16Lvl_limits_hihi_alm_out | Bin 16 Level High-High Alarm | lazy_b | grain | ¦{register:grain:g_bin16Lvl_limits_hihi_alm_out}¦ | 1 | "Bin 16 Level High-High Alarm, at " + Math.round(¦{register:grain:g_bin16Lvl_out_eu}¦) + "%" | "Bin 16 Level High-High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin16Lvl_limits_hi_alm_out | Bin 16 Level High Alarm | lazy_b | grain | ¦{register:grain:g_bin16Lvl_limits_hi_alm_out}¦ | 1 | "Bin 16 Level High Alarm, at " + Math.round(¦{register:grain:g_bin16Lvl_out_eu}¦) + "%" | "Bin 16 Level High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin16Lvl_limits_lo_alm_out | Bin 16 Level Low Alarm | lazy_b | grain | ¦{register:grain:g_bin16Lvl_limits_lo_alm_out}¦ | 1 | "Bin 16 Level Low Alarm, at " + Math.round(¦{register:grain:g_bin16Lvl_out_eu}¦) + "%" | "Bin 16 Level Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin16Lvl_limits_lolo_alm_out | Bin 16 Level Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_bin16Lvl_limits_lolo_alm_out}¦ | 1 | "Bin 16 Level Low-Low Alarm, at " + Math.round(¦{register:grain:g_bin16Lvl_out_eu}¦) + "%" | "Bin 16 Level Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin17Lvl_faults_over_out | Bin 17 Level Sensor Overrange Fault | lazy_b | grain | ¦{register:grain:g_bin17Lvl_faults_over_out}¦ | 1 | "Bin 17 Level Sensor Overrange Fault, reading " + Math.round(¦{register:grain:g_bin17Lvl_out_eu}¦) + "%" | "Bin 17 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin17Lvl_faults_under_out | Bin 17 Level Sensor Underrange Fault | lazy_b | grain | ¦{register:grain:g_bin17Lvl_faults_under_out}¦ | 1 | "Bin 17 Level Sensor Underrange Fault, reading " + Math.round(¦{register:grain:g_bin17Lvl_out_eu}¦) + "%" | "Bin 17 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin17Lvl_faults_chan_out | Bin 17 Level Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_bin17Lvl_faults_chan_out}¦ | 1 | "Bin 17 Level Sensor Channel Fault" | "Bin 17 Level Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin17Lvl_limits_hihi_alm_out | Bin 17 Level High-High Alarm | lazy_b | grain | ¦{register:grain:g_bin17Lvl_limits_hihi_alm_out}¦ | 1 | "Bin 17 Level High-High Alarm, at " + Math.round(¦{register:grain:g_bin17Lvl_out_eu}¦) + "%" | "Bin 17 Level High-High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin17Lvl_limits_hi_alm_out | Bin 17 Level High Alarm | lazy_b | grain | ¦{register:grain:g_bin17Lvl_limits_hi_alm_out}¦ | 1 | "Bin 17 Level High Alarm, at " + Math.round(¦{register:grain:g_bin17Lvl_out_eu}¦) + "%" | "Bin 17 Level High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin17Lvl_limits_lo_alm_out | Bin 17 Level Low Alarm | lazy_b | grain | ¦{register:grain:g_bin17Lvl_limits_lo_alm_out}¦ | 1 | "Bin 17 Level Low Alarm, at " + Math.round(¦{register:grain:g_bin17Lvl_out_eu}¦) + "%" | "Bin 17 Level Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin17Lvl_limits_lolo_alm_out | Bin 17 Level Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_bin17Lvl_limits_lolo_alm_out}¦ | 1 | "Bin 17 Level Low-Low Alarm, at " + Math.round(¦{register:grain:g_bin17Lvl_out_eu}¦) + "%" | "Bin 17 Level Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin18Lvl_faults_over_out | Bin 18 Level Sensor Overrange Fault | lazy_b | grain | ¦{register:grain:g_bin18Lvl_faults_over_out}¦ | 1 | "Bin 18 Level Sensor Overrange Fault, reading " + Math.round(¦{register:grain:g_bin18Lvl_out_eu}¦) + "%" | "Bin 18 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin18Lvl_faults_under_out | Bin 18 Level Sensor Underrange Fault | lazy_b | grain | ¦{register:grain:g_bin18Lvl_faults_under_out}¦ | 1 | "Bin 18 Level Sensor Underrange Fault, reading " + Math.round(¦{register:grain:g_bin18Lvl_out_eu}¦) + "%" | "Bin 18 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin18Lvl_faults_chan_out | Bin 18 Level Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_bin18Lvl_faults_chan_out}¦ | 1 | "Bin 18 Level Sensor Channel Fault" | "Bin 18 Level Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin18Lvl_limits_hihi_alm_out | Bin 18 Level High-High Alarm | lazy_b | grain | ¦{register:grain:g_bin18Lvl_limits_hihi_alm_out}¦ | 1 | "Bin 18 Level High-High Alarm, at " + Math.round(¦{register:grain:g_bin18Lvl_out_eu}¦) + "%" | "Bin 18 Level High-High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin18Lvl_limits_hi_alm_out | Bin 18 Level High Alarm | lazy_b | grain | ¦{register:grain:g_bin18Lvl_limits_hi_alm_out}¦ | 1 | "Bin 18 Level High Alarm, at " + Math.round(¦{register:grain:g_bin18Lvl_out_eu}¦) + "%" | "Bin 18 Level High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin18Lvl_limits_lo_alm_out | Bin 18 Level Low Alarm | lazy_b | grain | ¦{register:grain:g_bin18Lvl_limits_lo_alm_out}¦ | 1 | "Bin 18 Level Low Alarm, at " + Math.round(¦{register:grain:g_bin18Lvl_out_eu}¦) + "%" | "Bin 18 Level Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin18Lvl_limits_lolo_alm_out | Bin 18 Level Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_bin18Lvl_limits_lolo_alm_out}¦ | 1 | "Bin 18 Level Low-Low Alarm, at " + Math.round(¦{register:grain:g_bin18Lvl_out_eu}¦) + "%" | "Bin 18 Level Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin19Lvl_faults_over_out | Bin 19 Level Sensor Overrange Fault | lazy_b | grain | ¦{register:grain:g_bin19Lvl_faults_over_out}¦ | 1 | "Bin 19 Level Sensor Overrange Fault, reading " + Math.round(¦{register:grain:g_bin19Lvl_out_eu}¦) + "%" | "Bin 19 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin19Lvl_faults_under_out | Bin 19 Level Sensor Underrange Fault | lazy_b | grain | ¦{register:grain:g_bin19Lvl_faults_under_out}¦ | 1 | "Bin 19 Level Sensor Underrange Fault, reading " + Math.round(¦{register:grain:g_bin19Lvl_out_eu}¦) + "%" | "Bin 19 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin19Lvl_faults_chan_out | Bin 19 Level Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_bin19Lvl_faults_chan_out}¦ | 1 | "Bin 19 Level Sensor Channel Fault" | "Bin 19 Level Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin19Lvl_limits_hihi_alm_out | Bin 19 Level High-High Alarm | lazy_b | grain | ¦{register:grain:g_bin19Lvl_limits_hihi_alm_out}¦ | 1 | "Bin 19 Level High-High Alarm, at " + Math.round(¦{register:grain:g_bin19Lvl_out_eu}¦) + "%" | "Bin 19 Level High-High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin19Lvl_limits_hi_alm_out | Bin 19 Level High Alarm | lazy_b | grain | ¦{register:grain:g_bin19Lvl_limits_hi_alm_out}¦ | 1 | "Bin 19 Level High Alarm, at " + Math.round(¦{register:grain:g_bin19Lvl_out_eu}¦) + "%" | "Bin 19 Level High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin19Lvl_limits_lo_alm_out | Bin 19 Level Low Alarm | lazy_b | grain | ¦{register:grain:g_bin19Lvl_limits_lo_alm_out}¦ | 1 | "Bin 19 Level Low Alarm, at " + Math.round(¦{register:grain:g_bin19Lvl_out_eu}¦) + "%" | "Bin 19 Level Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin19Lvl_limits_lolo_alm_out | Bin 19 Level Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_bin19Lvl_limits_lolo_alm_out}¦ | 1 | "Bin 19 Level Low-Low Alarm, at " + Math.round(¦{register:grain:g_bin19Lvl_out_eu}¦) + "%" | "Bin 19 Level Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin20Lvl_faults_over_out | Bin 20 Level Sensor Overrange Fault | lazy_b | grain | ¦{register:grain:g_bin20Lvl_faults_over_out}¦ | 1 | "Bin 20 Level Sensor Overrange Fault, reading " + Math.round(¦{register:grain:g_bin20Lvl_out_eu}¦) + "%" | "Bin 20 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin20Lvl_faults_under_out | Bin 20 Level Sensor Underrange Fault | lazy_b | grain | ¦{register:grain:g_bin20Lvl_faults_under_out}¦ | 1 | "Bin 20 Level Sensor Underrange Fault, reading " + Math.round(¦{register:grain:g_bin20Lvl_out_eu}¦) + "%" | "Bin 20 Level Sensor Back In Range" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin20Lvl_faults_chan_out | Bin 20 Level Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_bin20Lvl_faults_chan_out}¦ | 1 | "Bin 20 Level Sensor Channel Fault" | "Bin 20 Level Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin20Lvl_limits_hihi_alm_out | Bin 20 Level High-High Alarm | lazy_b | grain | ¦{register:grain:g_bin20Lvl_limits_hihi_alm_out}¦ | 1 | "Bin 20 Level High-High Alarm, at " + Math.round(¦{register:grain:g_bin20Lvl_out_eu}¦) + "%" | "Bin 20 Level High-High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin20Lvl_limits_hi_alm_out | Bin 20 Level High Alarm | lazy_b | grain | ¦{register:grain:g_bin20Lvl_limits_hi_alm_out}¦ | 1 | "Bin 20 Level High Alarm, at " + Math.round(¦{register:grain:g_bin20Lvl_out_eu}¦) + "%" | "Bin 20 Level High Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin20Lvl_limits_lo_alm_out | Bin 20 Level Low Alarm | lazy_b | grain | ¦{register:grain:g_bin20Lvl_limits_lo_alm_out}¦ | 1 | "Bin 20 Level Low Alarm, at " + Math.round(¦{register:grain:g_bin20Lvl_out_eu}¦) + "%" | "Bin 20 Level Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_bin20Lvl_limits_lolo_alm_out | Bin 20 Level Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_bin20Lvl_limits_lolo_alm_out}¦ | 1 | "Bin 20 Level Low-Low Alarm, at " + Math.round(¦{register:grain:g_bin20Lvl_out_eu}¦) + "%" | "Bin 20 Level Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m01_fault_out | M01 Fault | lazy_b | grain | ¦{register:grain:g_m01_fault_out}¦ | 1 | "Truck Drag Fault: " + ({0:"No alarm",1:"Communication fault",2:"Internal drive fault",3:"External fault input active",4:"Motor overload",5:"Drive (inverter) overload",6:"Undervoltage",7:"Overvoltage",8:"Overcurrent",9:"Ground fault",10:"Power loss",11:"Output phase loss",12:"Drive overtemperature",13:"Local control active (remote control not available)",14:"Drive Comm Fault",15:"Safe Torque Off",99:"Unknown fault"}[¦{register:grain:g_m01_out_faultVFDId_last}¦] ¦¦ "Unknown fault") | "Truck Drag Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m03_fault_out | M03 Fault | lazy_b | grain | ¦{register:grain:g_m03_fault_out}¦ | 1 | "Receiving Grain Pump Fault: " + ({0:"No alarm",1:"Communication fault",2:"Internal drive fault",3:"External fault input active",4:"Motor overload",5:"Drive (inverter) overload",6:"Undervoltage",7:"Overvoltage",8:"Overcurrent",9:"Ground fault",10:"Power loss",11:"Output phase loss",12:"Drive overtemperature",13:"Local control active (remote control not available)",14:"Drive Comm Fault",15:"Safe Torque Off",99:"Unknown fault"}[¦{register:grain:g_m03_out_faultVFDId_last}¦] ¦¦ "Unknown fault") | "Receiving Grain Pump Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m04_fault_out | M04 Fault | lazy_b | grain | ¦{register:grain:g_m04_fault_out}¦ | 1 | "Distribution Loop Fault: " + ({0:"No alarm",1:"Communication fault",2:"Internal drive fault",3:"External fault input active",4:"Motor overload",5:"Drive (inverter) overload",6:"Undervoltage",7:"Overvoltage",8:"Overcurrent",9:"Ground fault",10:"Power loss",11:"Output phase loss",12:"Drive overtemperature",13:"Local control active (remote control not available)",14:"Drive Comm Fault",15:"Safe Torque Off",99:"Unknown fault"}[¦{register:grain:g_m04_out_faultVFDId_last}¦] ¦¦ "Unknown fault") | "Distribution Loop Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m05_stalled_out | M05 Stalled | lazy_b | grain | ¦{register:grain:g_m05_stalled_out}¦ | 1 | "Rotary Discharge Bin 13 Stalled" | "Rotary Discharge Bin 13 Stall Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m01HSC_fault_out | M01 HSC Fault | lazy_b | grain | ¦{register:grain:g_m01HSC_fault_out}¦ | 1 | "Truck Drag High Speed Counter Fault" | "Truck Drag High Speed Counter Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m01Spd_faults_chan_out | M01 Speed Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m01Spd_faults_chan_out}¦ | 1 | "Truck Drag Speed Sensor Channel Fault" | "Truck Drag Speed Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m01Spd_limits_lo_alm_out | M01 Speed Low Alarm | lazy_b | grain | ¦{register:grain:g_m01Spd_limits_lo_alm_out}¦ | 1 | "Truck Drag Speed Low Alarm, at " + Math.round(¦{register:grain:g_m01Spd_out_eu}¦) | "Truck Drag Speed Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m01Spd_limits_lolo_alm_out | M01 Speed Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_m01Spd_limits_lolo_alm_out}¦ | 1 | "Truck Drag Speed Low-Low Alarm, at " + Math.round(¦{register:grain:g_m01Spd_out_eu}¦) | "Truck Drag Speed Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m02HSC_fault_out | M02 HSC Fault | lazy_b | grain | ¦{register:grain:g_m02HSC_fault_out}¦ | 1 | "Receiving Drag High Speed Counter Fault" | "Receiving Drag High Speed Counter Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m02Spd_faults_chan_out | M02 Speed Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m02Spd_faults_chan_out}¦ | 1 | "Receiving Drag Speed Sensor Channel Fault" | "Receiving Drag Speed Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m02Spd_limits_lo_alm_out | M02 Speed Low Alarm | lazy_b | grain | ¦{register:grain:g_m02Spd_limits_lo_alm_out}¦ | 1 | "Receiving Drag Speed Low Alarm, at " + Math.round(¦{register:grain:g_m02Spd_out_eu}¦) | "Receiving Drag Speed Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m02Spd_limits_lolo_alm_out | M02 Speed Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_m02Spd_limits_lolo_alm_out}¦ | 1 | "Receiving Drag Speed Low-Low Alarm, at " + Math.round(¦{register:grain:g_m02Spd_out_eu}¦) | "Receiving Drag Speed Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m04HSC_fault_out | M04 HSC Fault | lazy_b | grain | ¦{register:grain:g_m04HSC_fault_out}¦ | 1 | "Distribution Loop High Speed Counter Fault" | "Distribution Loop High Speed Counter Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m04Spd_faults_chan_out | M04 Speed Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m04Spd_faults_chan_out}¦ | 1 | "Distribution Loop Speed Sensor Channel Fault" | "Distribution Loop Speed Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m04Spd_limits_lo_alm_out | M04 Speed Low Alarm | lazy_b | grain | ¦{register:grain:g_m04Spd_limits_lo_alm_out}¦ | 1 | "Distribution Loop Speed Low Alarm, at " + Math.round(¦{register:grain:g_m04Spd_out_eu}¦) | "Distribution Loop Speed Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m04Spd_limits_lolo_alm_out | M04 Speed Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_m04Spd_limits_lolo_alm_out}¦ | 1 | "Distribution Loop Speed Low-Low Alarm, at " + Math.round(¦{register:grain:g_m04Spd_out_eu}¦) | "Distribution Loop Speed Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m30HSC_fault_out | M30 HSC Fault | lazy_b | grain | ¦{register:grain:g_m30HSC_fault_out}¦ | 1 | "Reclaim Drag South High Speed Counter Fault" | "Reclaim Drag South High Speed Counter Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m30Spd_faults_chan_out | M30 Speed Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m30Spd_faults_chan_out}¦ | 1 | "Reclaim Drag South Speed Sensor Channel Fault" | "Reclaim Drag South Speed Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m30Spd_limits_lo_alm_out | M30 Speed Low Alarm | lazy_b | grain | ¦{register:grain:g_m30Spd_limits_lo_alm_out}¦ | 1 | "Reclaim Drag South Speed Low Alarm, at " + Math.round(¦{register:grain:g_m30Spd_out_eu}¦) | "Reclaim Drag South Speed Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m30Spd_limits_lolo_alm_out | M30 Speed Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_m30Spd_limits_lolo_alm_out}¦ | 1 | "Reclaim Drag South Speed Low-Low Alarm, at " + Math.round(¦{register:grain:g_m30Spd_out_eu}¦) | "Reclaim Drag South Speed Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m03HSC_fault_out | M03 HSC Fault | lazy_b | grain | ¦{register:grain:g_m03HSC_fault_out}¦ | 1 | "Receiving Pump High Speed Counter Fault" | "Receiving Pump High Speed Counter Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m03Spd_faults_chan_out | M03 Speed Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m03Spd_faults_chan_out}¦ | 1 | "Receiving Pump Speed Sensor Channel Fault" | "Receiving Pump Speed Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m03Spd_limits_lo_alm_out | M03 Speed Low Alarm | lazy_b | grain | ¦{register:grain:g_m03Spd_limits_lo_alm_out}¦ | 1 | "Receiving Pump Speed Low Alarm, at " + Math.round(¦{register:grain:g_M03Spd_out_eu}¦) | "Receiving Pump Speed Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m03Spd_limits_lolo_alm_out | M03 Speed Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_m03Spd_limits_lolo_alm_out}¦ | 1 | "Receiving Pump Speed Low-Low Alarm, at " + Math.round(¦{register:grain:g_M03Spd_out_eu}¦) | "Receiving Pump Speed Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m29HSC_fault_out | M29 HSC Fault | lazy_b | grain | ¦{register:grain:g_m29HSC_fault_out}¦ | 1 | "Reclaim Drag North High Speed Counter Fault" | "Reclaim Drag North High Speed Counter Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m29Spd_faults_chan_out | M29 Speed Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m29Spd_faults_chan_out}¦ | 1 | "Reclaim Drag North Speed Sensor Channel Fault" | "Reclaim Drag North Speed Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m29Spd_limits_lo_alm_out | M29 Speed Low Alarm | lazy_b | grain | ¦{register:grain:g_m29Spd_limits_lo_alm_out}¦ | 1 | "Reclaim Drag North Speed Low Alarm, at " + Math.round(¦{register:grain:g_M29Spd_out_eu}¦) | "Reclaim Drag North Speed Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m29Spd_limits_lolo_alm_out | M29 Speed Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_m29Spd_limits_lolo_alm_out}¦ | 1 | "Reclaim Drag North Speed Low-Low Alarm, at " + Math.round(¦{register:grain:g_M29Spd_out_eu}¦) | "Reclaim Drag North Speed Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m31HSC_fault_out | M31 HSC Fault | lazy_b | grain | ¦{register:grain:g_m31HSC_fault_out}¦ | 1 | "Reclaim Pump High Speed Counter Fault" | "Reclaim Pump High Speed Counter Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m31Spd_faults_chan_out | M31 Speed Sensor Channel Fault | lazy_b | grain | ¦{register:grain:g_m31Spd_faults_chan_out}¦ | 1 | "Reclaim Pump Speed Sensor Channel Fault" | "Reclaim Pump Speed Sensor Channel Restored" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m31Spd_limits_lo_alm_out | M31 Speed Low Alarm | lazy_b | grain | ¦{register:grain:g_m31Spd_limits_lo_alm_out}¦ | 1 | "Reclaim Pump Speed Low Alarm, at " + Math.round(¦{register:grain:g_M31Spd_out_eu}¦) | "Reclaim Pump Speed Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m31Spd_limits_lolo_alm_out | M31 Speed Low-Low Alarm | lazy_b | grain | ¦{register:grain:g_m31Spd_limits_lolo_alm_out}¦ | 1 | "Reclaim Pump Speed Low-Low Alarm, at " + Math.round(¦{register:grain:g_M31Spd_out_eu}¦) | "Reclaim Pump Speed Low-Low Alarm Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_esdCircOut_fault_out | ESC Circuit Fault | lazy_b | grain | ¦{register:grain:g_esdCircOut_fault_out}¦ | 1 | "ESD Circuit Output Fault" | "ESD Circuit Output Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_recRpdStp_out | Receiving Rapid Stop | lazy_b | grain | ¦{register:grain:g_recRpdStp_out}¦ | 1 | "Receiving Rapid Stop" | "Rapid Stop Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_m31_fault_out | M31 Fault | lazy_b | grain | ¦{register:grain:g_m31_fault_out}¦ | 1 | "Reclaim Pump Fault: " + ({0:"No alarm",1:"Communication fault",2:"Internal drive fault",3:"External fault input active",4:"Motor overload",5:"Drive (inverter) overload",6:"Undervoltage",7:"Overvoltage",8:"Overcurrent",9:"Ground fault",10:"Power loss",11:"Output phase loss",12:"Drive overtemperature",13:"Local control active (remote control not available)",14:"Drive Comm Fault",15:"Safe Torque Off",99:"Unknown fault"}[¦{register:grain:g_m31_out_faultVFDId_last}¦] ¦¦ "Unknown fault") | "Reclaim Pump Fault Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_esdHMI_out | HMI ESD | lazy_b | grain | ¦{register:grain:g_esdHMI_out}¦ | 1 | "HMI ESD Pressed" | "HMI ESD Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
g_esdSum_out | ESD | lazy_b | grain | ¦{register:grain:g_esdSum_out}¦ | 1 | "ESD" | "ESD Cleared" | 2 | FALSE | 0 | 0 | TRUE | ["43072529-dab4-4518-99fe-e6014e7ba93b","961886d0-3127-4fb9-90a5-316d353cdca0"]
Note on I1: 0=Info 1=Warning 2=Critical